## 1 Background Noise by persons
Number of (active) persons → | 1000 | Background Noise Level Calculation Tool, Version 1.07 Persons
Room Volume [m³] → | 1000
Octave Band values | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2kHz | 4 kHz | 8 kHz
RT60 [s] → | 1 | 1 | 1 | 1 | 1 | 1 | 1
Sound Power Levels LW [dB ] (*1) | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2kHz | 4 kHz | 8 kHz | dB (Z) | dB(A)
normal speech | 55 | 65.3 | 69 | 63 | 55.8 | 49.8 | 44.5 | 71.5 | 68.4
raised spreech | 60 | 69.5 | 74.9 | 71.9 | 63.8 | 57.3 | 48.4 | 77.7 | 75.5
loud speech | 64 | 72.1 | 79.6 | 80.2 | 72.9 | 65.9 | 54.8 | 83.8 | 82.6
shouted speech | 65 | 73.1 | 84 | 89.3 | 82.4 | 74.9 | 64.1 | 91.2 | 90.9
Noise-Level Results Ln in dB SPL | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2kHz | 4 kHz | 8 kHz | dB (Z) | dB(A)
normal | 68.9523 | 79.2523 | 82.9523 | 76.9523 | 69.7523 | 63.7523 | 58.4523 | 85.459 | 82.3509
Sum of 10*Antilog | 7.8566e-06 | 8.4185e-05 | 0.00019735 | 4.9572e-05 | 9.4457e-06 | 2.3727e-06 | 7.0022e-07
A-weighting (dB) | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | 0.00035148
Weighted bands | 52.8523 | 70.6523 | 79.7523 | 76.9523 | 70.9523 | 64.7523 | 57.3523
Sum of 10*Antilog | 1.9286e-07 | 1.1621e-05 | 9.4457e-05 | 4.9572e-05 | 1.2452e-05 | 2.987e-06 | 5.4354e-07 | 0.00017182
raised | 73.9523 | 83.4523 | 88.8523 | 85.8523 | 77.7523 | 71.2523 | 62.3523 | 91.6835 | 89.4456
| 2.4845e-05 | 0.00022143 | 0.00076778 | 0.0003848 | 5.9598e-05 | 1.3342e-05 | 1.7188e-06
| -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | 0.0014735
| 57.8523 | 74.8523 | 85.6523 | 85.8523 | 78.9523 | 72.2523 | 61.2523
| 6.0987e-07 | 3.0566e-05 | 0.00036748 | 0.0003848 | 7.8566e-05 | 1.6797e-05 | 1.3342e-06 | 0.00088015
loud | 77.9523 | 86.0523 | 93.5523 | 94.1523 | 86.8523 | 79.8523 | 68.7523 | 97.7242 | 96.5411
| 6.2407e-05 | 0.00040293 | 0.0022659 | 0.0026016 | 0.00048443 | 9.6657e-05 | 7.503e-06
| -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | 0.0059214
| 61.8523 | 77.4523 | 90.3523 | 94.1523 | 88.0523 | 80.8523 | 67.6523
| 1.5319e-06 | 5.562e-05 | 0.0010845 | 0.0026016 | 0.00063861 | 0.00012168 | 5.8242e-06 | 0.0045093
shouted | 78.9523 | 87.0523 | 97.9523 | 103.2523 | 96.3523 | 88.8523 | 78.0523 | 105.2012 | 104.9014
| 7.8566e-05 | 0.00050726 | 0.0062407 | 0.021146 | 0.0043175 | 0.00076778 | 6.3861e-05
| -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | 0.033122
| 62.8523 | 78.4523 | 94.7523 | 103.2523 | 97.5523 | 89.8523 | 76.9523
| 1.9286e-06 | 7.0022e-05 | 0.002987 | 0.021146 | 0.0056916 | 0.00096657 | 4.9572e-05 | 0.030913
Remarks: | Are all people talking? At which level are they talking? Is there any machninery that is producing sigificant noise during voice alarm?
*1 Sound Power Level sources: a ) ANSI 3.5-1997. Methods for Calculation of the Speech Intelligibility Index. American National Standard. New York (Reaffirmed in 2007). b) J.H. Rindel, C.L. Christensen, A.C. Gade: Dynamic sound source for simulating the Lombard effect in room acoustic modeling software. Proceedings of Internoise 2012, New York, 2012.
Note on B11: Octave Noise Levels in dB SPL for diffuse sound field Lr

## 2 Background Noise by Lw (Machi
Number of sources (e.g.machines)→ | 1 | Background Noise Level Calculation Tool, Version 1.07 Lw
Room Volume [m³] → | 3840
Octave Band values | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2kHz | 4 kHz | 8 kHz
RT60 [s] → | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Power Level from machinery | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2kHz | 4 kHz | 8 kHz | dB (Z) | dB(A)
Sound Power Levels LW [dB ] (*2)→ | 111.5 | 111.5 | 111.5 | 111.5 | 111.5 | 111.5 | 111.5 | 119.951 | 118.485
| 0.14125 | 0.14125 | 0.14125 | 0.14125 | 0.14125 | 0.14125 | 0.14125
| -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | 0.98878
| 95.4 | 102.9 | 108.3 | 111.5 | 112.7 | 112.5 | 110.4
| 0.0034674 | 0.019498 | 0.067608 | 0.14125 | 0.18621 | 0.17783 | 0.10965 | 0.70551
Noise-Level Results Ln in dB SPL | 125 Hz | 250 Hz | 500 Hz | 1 kHz | 2kHz | 4 kHz | 8 kHz | dB (Z) | dB(A)
from Machinery (calculated from Lw) | 91.3699 | 91.3699 | 91.3699 | 91.3699 | 91.3699 | 91.3699 | 91.3699 | 99.8209 | 98.355
Sum of 10*Antilog | 0.0013709 | 0.0013709 | 0.0013709 | 0.0013709 | 0.0013709 | 0.0013709 | 0.0013709
A-weighting (dB) | -16.1 | -8.6 | -3.2 | 0 | 1.2 | 1 | -1.1 | 0.009596
Weighted bands | 75.2699 | 82.7699 | 88.1699 | 91.3699 | 92.5699 | 92.3699 | 90.2699
Sum of 10*Antilog | 3.3651e-05 | 0.00018923 | 0.00065614 | 0.0013709 | 0.0018071 | 0.0017258 | 0.0010641 | 0.006847
103
[10 empty] | 7 | -8.451
Remarks: | Te example is 1 Watt of acoustical Power forr all octave bands. Is the machninery that is producing noise during voice alarm? Are there people talking with sigificant level during voice alarm?
*2) input is Sound Power Level referenced to Lw = 0 dB for 10 -12 W ¦ Output result is Sound Pressure Level referenced to L = 0 dB for 20 -6 Pa !
Note on B13: Octave Noise Levels in dB SPL for diffuse sound field Lr

## Manual, Credits, Copyright
Background Noise Level Calculation Tool, Version 1.07
Background Noise Level Calculation Tool for rooms with with exponential reverberation
This Excel tool calculates the Sound Pressure Level (SPL) of background noise diffuse field Lr for rooms with exponential reverberation as a function of the number of people talking with a variety of speech levels or as a function of Noise Power Levels Lw (like from machinery, exhaust fans etc) in octave bands. It also indicates the A-weighted and Z-weighted Levels of the diffuse sound field for all octave bands.
The basis for the calculation is that each octave band filtered impulse response for the room has an exponential form and can thus be characterised by a reverberation time. The acoustic system is also assumed to be linear and time invariant. The calulation tool should not be used as an alternative to real world measurements, if possible!
For using the tool - enter input values in the green fields on Tab „1 Backgrond Noise by persons“:
Number of (active) persons: enter number of people talking normal, with raised speech level …
Room Volume [m³]: Enter the room volume in cubic meters
RT60 [s]: Enter the RT60 figures in seconds for all octave bands.
Noise-Level Results Ln in dB SPL: are the calculated Background Noise Level results for all octave bands and the A-weighted and Z-weighted results.
or
For using the tool - enter input values in the green fields on Tab „2 Backgrond Noise by Lw (Machinery)“:
Number of (active) machines: enter number of machines producing background noise
Room Volume [m³]: Enter the room volume in cubic meters
RT60 [s]: Enter the RT60 figures in seconds for all octave bands.
Sound Power Levels LW [dB ]: Enter the Lw figures of machinery or other sources for all octave bands.
Noise-Level Results Ln in dB SPL: are the calculated Background Noise Level results for all octave bands and the A-weighted and Z-weighted results.
This tool is intended to be used with ULYSSES 2.90 Software and PAUL 1.07 and has originally been written by:
Volker Löwer
IFBsoft GbR
Ginsheimer Str. 1
65462 Ginsheim-Gustavsburg
Germany
Mail: info@ifbsoft.de
Date: 2025-11-03
Copyright for this tool belongs to IFBsoft. The tool can be copied and used freely as long as not sold. IFBsoft takes no responsibility for errors in the calculation or use of results.